Blue-White A100NVP Peristaltic Metering Pump

- METERING PUMP – Shall be a positive displacement, peristaltic type tubing pump with a variable speed motor, non-spring loaded roller assembly located in the pumphead, integral tube failure detection system, and flexible tubing with attached connection fittings.

  - There shall be no valves, diaphragms, springs, or dynamic seals in the fluid path. Process fluid shall contact the pump tubing assembly and connection fittings only.

  - Capable of self priming at the rated maximum pressure.

  - Capable of running dry without damage.

  - Suction lift shall be 30 feet of water.

  - Pump shall have a one year manufacturer’s warranty that includes chemical damage to the pump head and roller assembly caused by a ruptured pump tube assembly.

- PUMPHEAD – Shall be a single, unbroken track with a clear removable cover.

  - Optical tube failure detection sensor shall be wholly located in the pumphead. Sensor shall be capable of detecting water and oil based chemicals. Float switch type switches shall not be used. Process fluid waste ports or leak drains shall not be provided.

  - Squeeze rollers shall be directly coupled to a one piece Valox 420 SEO rotor. Three polymeric squeeze rollers located 120 degrees apart shall be provided. The roller diameters and occlusion gap shall be factory set to provide the optimum tubing compression; field adjustment shall not be required. Spring loaded or hinged rollers shall not be used.

  - Rotor assembly shall be installed on a D-shaped, chrome plated motor shaft and removable without tools.

  - For tubing installation and removal, rotor assembly shall be rotated by the motor drive. Hand cranking of the rotor assembly shall not be required.

  - Pump head and tubing compression surface shall be corrosion resistant Valox 420 SEO thermoplastic.

  - The pump head cover shall be clear thermoplastic with an integral bearing fitted to support the overhung load on the motor shaft.

  - Cover shall be positively secured to the pump head using three thumb screws. Tools shall not be required to remove the pump head cover.

- PUMP TUBE ASSEMBLY

  - To ensure pump performance and accuracy, only tubing provided by the manufacturer is acceptable.

  - Pump tube shall be assembled to connection fittings of PVDF material.

  - Connection fittings shall be permanently clamped to the tubing with stainless steel clamps. To prevent tubing misalignment and ensure accuracy, fittings shall insert into keyed slots located in the pump head and secured in place by the pump head cover. Fitting shall not rotate when installed.

  - Connection fittings shall accept 1/4” ID x 3/8” OD flexible tubing.

  - Tube sizes and connections shall be measured in inches.

  - The following tube sizes shall be available:

- DRIVE SYSTEM – Shall be factory installed and totally enclosed in a NEMA 3R, outdoor rated enclosure.

  - Motor

    - DC gearmotor rated for continuous duty.

    - Motor shall include overload protection.

    - Four maximum RPM gear ratio options shall be provided; 14 RPM, 30 RPM, 45 RPM, and 60 RPM. (Engineer to specify)

    - Variable speed motor shall be adjustable from 10% to 100% in 1% increments.

    - Motor shall continuously rotate over the entire adjustment range; start/stop pulsation shall not be permitted.

  - Enclosure

    - Material shall be injection molded Valox 420 SEO.

    - Enclosure shall be rated NEMA 3R.

    - Provided with four slots in the enclosure base for shelf mounting and two slots in the rear panel for wall mounting. Stainless steel mounting hardware shall be provided.

    - Provide six foot length power supply cord with NEMA 5/15 U.S. 115VAC attachment plug. Optional: power supply cord with NEMA 6/15 U.S. 230 VAC attachment plug. (Engineer to specify)

    - A wiring compartment shall be provided for connection of input/output signal wires, and alarm output load. Conduit hubs, liquid-tight connectors, connector through holes and tapped holes shall be sized in U.S. inches.

  - Control Circuitry.

    - Provide front panel user touchpad controls for stop/start, configuration menu access and navigation, operating mode selection, auto priming, and service timer reset.

    - To prevent tampering, the front panel touchpad and LCD display shall be wholly enclosed by a clear acrylic door secured by two slide clamps.

    - Provide LCD display for menu driven configuration settings, pump output value, service alerts, tube failure detection (TFD) system and flow verification system (FVS) alarms status, remote input signal values, tubing life timer value.

    - Provide for manual control of pump output volume via manual speed percentage operating mode.

    - Provide for remote control of pump output volume via 4-20mA, 0-10VDC, and 0-1000Hz pulse operating modes.

    - Provide one contact closure alarm output rated at 1A-250VAC, 0.8A-30VDC. Alarm output shall close in the event that either the Tube Failure Detection (TFD) system or the Flow Verification System (FVS) pump systems are triggered.

    - Provide a flow verification system (FVS) with programmable alarm delay time from 1-256 seconds. FVS system shall monitor the FVS flow sensor while pump is running only. System shall not monitor pump while not running.

- FLOW VERIFICATION SENSOR (optional) – Shall output high speed digital pulse signal, while pump is running only, to verify chemical injection.

  - Flow verification sensor shall be a paddlewheel type sensor.

  - Sensor body, paddle, lens cap, and axle material shall be PVDF.

  - Inlet and outlet fitting connections shall accept 1/4” ID x 3/8” OD flexible tubing and shall be PVDF.

  - Sensor operating range shall be as follows: (Engineer to specify)

Code		Operating Range (GPH)		Operating Range (LPH)

100				0.47-4.7					1.78-17.8

200				1.6-15.8					6.0-60.5

300				3.2-31.7					12.1-121.0

400				4.7-47.5					17.8-177.7

500				7.9-79.2					29.9-298.6

600				11.1-110.9					42.0-419.6

- SAFETY

  - The pump shall be listed to UL standard 778 - Motor Operated Pump, CSA standard C22.2 - Process Control Equipment, and NSF/ANSI Standard 61 - Drinking Water System Components - Health Effects

  - Tube Failure Detection (TFD) sensor shall be wholly located in the pumphead. TFD system will stop the pump within three seconds of leak detection. To prevent false trigger from moisture the tube failure detection shall not trigger with water contact. Process fluid waste ports or leak drains shall not be provided.

- Manufacturer

  - The pump shall be Flex-Flo Model A-100NVP manufactured in the U.S.A. by Blue-White Industries.